## ABOUT
PKS Co-firing at an Indonesian Coal Power Plant — LCA and TEA Workbook
Study title | Life cycle assessment and techno-economic assessment of palm kernel shell (PKS) co-firing in a 300 MW sub-critical PLTU unit, Java-Bali system
Case study | PLTU Unit #2, 300 MW sub-critical, Java-Bali (Jamali) grid, Indonesia
Functional unit | 1 MWh net electricity delivered to the Java-Bali grid
Scenarios | 0% (baseline), 5%, 10%, 20% and 30% co-firing on an energy basis
Standards followed | ISO 14040:2006, ISO 14044:2006, ISO 14067:2018 (product carbon footprint)
LCIA method | ReCiPe 2016 v1.03 midpoint (H), proxy characterisation set
Background data | ecoinvent 3.10 proxy factors, Indonesia-specific where available
Foreground data | PLTU Unit #2 operating log 2025, CEMS record 2025, fuel laboratory results (ASTM D5865/D3174/D4239), PKS delivery logistics log, company visit 17 June 2025
TEA basis | Real-terms 2026 IDR, 25-year evaluation, 10% WACC, NPV of incremental cost divided by NPV of delivered energy
Currency | Indonesian rupiah (IDR) as primary; USD shown at a stated fixed rate
Model cross-check | All impact results reproduce the Brightway2 model in pks-cofiring-brightway/ to within 0.01 kg CO2e/MWh
Prepared by | Robby Fajrino Nugraha — Sustainability Data Analyst
Version | 1.0 — August 2026
COLOUR AND FORMAT CONVENTIONS
Blue text | Hardcoded input — change these to run your own case
Black text | Formula or calculation — do not overwrite
Green text | Link pulling a value from another worksheet
Yellow fill | Key assumption that should be reviewed before use
Sheet map
GOAL / SCOPE | ISO 14040 goal definition, system boundary, cut-off and allocation
PARAMETERS | All engineering inputs with sources — the only LCA inputs you need to edit
BACKGROUND / INDICATORS | Background (upstream) factors and ReCiPe characterisation factors
INVENTORY | Per-MWh life cycle inventory, computed from PARAMETERS for every scenario
IMPACT ASSESSMENT | Seven midpoint categories, foreground and background split
INTERPRETATION | Stage contribution, uncertainty, key drivers, conclusions
CAPEX / OPEX / FUEL PRICES | Techno-economic inputs under Indonesian 2026 conditions
CASH FLOW / LCOE | 25-year discounted cash flow and levelised cost of electricity
ABATEMENT COST | Cost of CO2e abatement, break-even PKS price, carbon price effect
SENSITIVITY | Tornado analysis and a two-way PKS price x coal price grid
DASHBOARD | One-page summary of LCA and TEA results
SOURCE GUIDE | Full source list for every literal used in the workbook

## GOAL
GOAL DEFINITION (ISO 14040 clause 5.2)
Intended application | Decision support for a state utility and an independent power producer evaluating biomass co-firing as a near-term decarbonisation measure for existing coal capacity, and for the emission-reduction claim reported under the national co-firing programme.
Reasons for the study | Co-firing is promoted as a low-cost abatement lever, but the claimed reduction depends on how the biogenic carbon, the upstream palm burden, the efficiency penalty and the transport route are treated. The study quantifies the net effect with a transparent, reproducible model.
Questions answered | 1) How much does the carbon footprint of 1 MWh fall per percentage point of co-firing? 2) Which life cycle stage and which parameter governs the result? 3) Is the reduction robust to data-quality uncertainty? 4) What does the abatement cost, and at what PKS price does it stop being economic?
Intended audience | Plant technical and sustainability management, utility planning, the ministry programme office, and an external critical reviewer.
Comparative assertion | Yes — scenarios are compared with each other. No comparative assertion is disclosed to the public against a competing product; results are reported with uncertainty ranges.
Limitations declared upfront | Background data are ecoinvent-3.10-consistent proxies, not licensed ecoinvent processes. Plant construction and decommissioning are cut off. Direct and indirect land-use change is not modelled; PKS is treated as an economically allocated residue.
Critical review | Internal review performed; the workbook and the underlying Brightway2 code are released so that an external reviewer can re-run every number.

## SCOPE
SCOPE, SYSTEM BOUNDARY AND METHODOLOGICAL CHOICES (ISO 14044 clause 4.2.3)
Function and functional unit
Function | Supply of dispatchable electrical energy to the Java-Bali transmission system
Functional unit | 1 MWh net electricity delivered to the grid
Reference flow | Fuel, reagents, transport and waste services required to deliver 1 MWh net
Time coverage | Operating year 2025; economics in real 2026 terms
Geography | Indonesia — plantation and mill in Sumatra/Kalimantan, plant on Java
Technology | 300 MW sub-critical pulverised-coal unit with ESP and wet FGD, direct co-firing through existing mills after crushing and drying
System boundary — unit processes included
Process | Stage | What it covers | Included?
P1_PKM | Upstream | Palm kernel shell at the mill gate, economically allocated (3.1% of mill revenue), including allocated plantation land occupation | Included
P2_Drying | Upstream | Drying to a target moisture content using biomass residue heat, plus crushing electricity and stockpile methane from storage | Included
P3_Transport | Transport | Road transport by 24 t diesel truck and, in the 30% case, coastal barge transport of 3 000 DWT | Included
P4_Handling | Core | Conveying, blending and milling at the plant — auxiliary electricity drawn from the grid model | Included
P5_Generation | Core | Boiler combustion of coal and PKS, FGD limestone supply, process and make-up water, stack emissions after ESP and FGD | Included
P6_Ash | Downstream | Controlled FABA landfilling of captured ash | Included
Plant construction | Capital | Civil works, boiler and turbine manufacture of the existing unit | Cut off
Retrofit hardware manufacture | Capital | Manufacture of the co-firing handling and drying equipment | Cut off (assessed in the TEA only)
Decommissioning | End of life | Dismantling and site remediation | Cut off
Land use change | Upstream | Direct and indirect LUC of the oil palm estate | Excluded — residue treatment, declared as a limitation
Methodological choices
Choice | Setting | Justification
Allocation | Economic allocation at the palm oil mill (3.1% to PKS) | PKS carries a real market price; ISO 14044 allocation hierarchy — subdivision is not possible, so allocation reflects the economic driver.
Biogenic carbon | Reported separately, characterisation factor 0 kg CO2e/kg | ISO 14067 requires fossil and biogenic carbon to be reported separately; the shells are a short-rotation residue.
Cut-off criteria | 1% of mass, energy or environmental relevance per flow; 5% cumulative | Standard practice; the cut-off flows are documented on the SOURCE GUIDE sheet.
Electricity background | Switchable — attributional average, marginal at time of use, marginal at time of construction, decarbonising 2040 | Auxiliary electricity is an ex-ante modelling choice, not a measurement; the switch shows how much the choice matters.
Multi-functionality of ash | FABA treated as waste to controlled landfill | Conservative; FABA valorisation as a cement substitute would credit the system and is not claimed.
Impact categories | Seven ReCiPe 2016 midpoints | Climate is the decision variable; the other six test for burden shifting.
Uncertainty | Pedigree-matrix lognormal uncertainty, 1 000 Monte Carlo iterations, Sobol variance decomposition | Data quality differs sharply between metered coal flow and literature stockpile methane.

## PARAMETERS
ENGINEERING PARAMETERS — the only LCA inputs you need to edit
Blue values are inputs. Every downstream sheet recalculates when you change them.
Parameter | Value | Unit | Source / basis
Lower heating value, coal (4200 kcal GAR) | 18.626 | MJ/kg | Laboratory mean of 2025 sample set, ASTM D5865
Lower heating value, PKS as received | 17.035 | MJ/kg | Laboratory mean of 2025 sample set, ASTM D5865
Ash content, coal (dry basis) | 0.055295 | kg/kg | Laboratory mean, ASTM D3174
Ash content, PKS (dry basis) | 0.030115 | kg/kg | Laboratory mean, ASTM D3174
Sulphur content, coal (dry basis) | 0.0040965 | kg/kg | Laboratory mean, ASTM D4239
Sulphur content, PKS (dry basis) | 0.0004885 | kg/kg | Laboratory mean, ASTM D4239
Nitrogen content, coal (dry basis) | 0.0095485 | kg/kg | Laboratory mean, ultimate analysis
Nitrogen content, PKS (dry basis) | 0.004059 | kg/kg | Laboratory mean, ultimate analysis
CO2 emission factor, coal | 94.6 | kg CO2/GJ | IPCC 2006 Vol. 2, sub-bituminous coal default
CO2 emission factor, PKS (biogenic) | 110 | kg CO2/GJ | IPCC 2006 Vol. 2, other primary solid biomass
CH4 emission factor, combustion | 0.001 | kg CH4/GJ | IPCC 2006, 1 g CH4/GJ
N2O emission factor, combustion | 0.0015 | kg N2O/GJ | IPCC 2006, 1.5 g N2O/GJ
NOx emission factor, coal firing | 0.1485 | kg NOx/GJ | CEMS Unit #2 annual mean 2025
SO2 emission factor after FGD | 0.19708 | kg SO2/GJ | CEMS 2025 with 90% FGD removal
PM2.5 emission factor after ESP | 0.008067 | kg PM2.5/GJ | Annual stack test, ESP 99.5% capture
Ash capture to controlled landfill | 0.905 | fraction | Ash balance, B3 landfill weighbridge 2025
FGD limestone per kg sulphur input | 1.407 | kg/kg S | FGD reagent store issue records
Auxiliary electricity, conveying and milling | 0.01204 | kWh/kg fuel | Plant own-use log 2025
Process and make-up water | 0.000165 | m3/MJ fuel | Water treatment plant balance
Drying heat demand, PKS | 0.85 | MJ/kg PKS | Dryer energy balance, company visit June 2025
Crushing electricity, PKS | 0.01808 | kWh/kg PKS | 75 kW crusher nameplate and throughput log
Stockpile methane from PKS storage | 0.00021973 | kg CH4/kg | Biomass storage literature — weakest data point
Allocated plantation land occupation | 0.42 | m2a/kg PKS | 3.8 t CPO/ha/yr productivity, economically allocated
PKS upstream burden per kg delivered | 1 | kg/kg | Economic allocation is embedded in the background factor
DERIVED PKS SCALING RATIOS (fuel-property based, black = formula)
Ratio | Value | Unit | Basis
NOx scaling, PKS vs coal | 0.42509 | - | Ratio of fuel-bound nitrogen
SO2 scaling, PKS vs coal | 0.11925 | - | Ratio of fuel sulphur
PM2.5 scaling, PKS vs coal | 0.54462 | - | Ratio of fuel ash
ELECTRICITY BACKGROUND MODEL (switchable)
Active mode number (1-4) | 1 |  | 1 = attributional average (default), 2 = marginal time of use, 3 = marginal time of construction, 4 = decarbonising 2040
# | Mode | GWP factor (kg CO2e/kWh) | Co-burden scale | Source
1 | Attributional grid average, time of use 2025 | 0.794 | 1 | KESDM Jamali grid emission factor 2025
2 | Marginal supplier, time of use (2025-2035) | 0.902 | 1.12 | Coal condensing sets the dispatch margin, RUPTL base case
3 | Marginal supplier, time of construction (2024) | 0.861 | 1.07 | Build-year marginal mix, coal with gas peaking
4 | Marginal supplier, decarbonising grid 2040 | 0.412 | 0.55 | Illustrative IAM-consistent pathway
Active GWP factor | 0.794
Active co-burden scale | 1
Active mode name | Attributional grid average, time of use 2025

## BACKGROUND
BACKGROUND (UPSTREAM) CHARACTERISED FACTORS
One row per background activity, already characterised per ReCiPe 2016 midpoint. Electricity rows read the active mode from PARAMETERS.
Background activity | Unit | GWP100 (kg CO2e) | Acidification (kg SO2e) | Photochem. ozone (kg NOxe) | PM formation (kg PM2.5e) | Freshwater eutroph. (kg Pe) | Land use (m2a) | Water (m3) | Data source
PKS upstream, economically allocated | kg | 0.043 | 0.00031 | 0.00018 | 0.0006 | 0.00012 | 0 | 0 | Agribalyse / Indonesian palm literature
Drying heat from biomass residue | MJ | 0.0042 | 9e-05 | 0.00021 | 0.0002 | 3e-05 | 0 | 0 | Biogenic heat, low fossil CO2
Crusher electricity (grid) | kWh | 0.794 | 0.0021 | 0.0013 | 0.0042 | 0.00072 | 0 | 0 | Jamali grid, active electricity mode
Truck transport, diesel 24 t | t.km | 0.152 | 0.00088 | 0.00055 | 0.0018 | 0.00028 | 0 | 0 | ecoinvent 3.10 proxy, freight lorry
Barge transport, 3000 DWT | t.km | 0.048 | 0.00042 | 0.0006 | 0.0009 | 9e-05 | 0 | 0 | ecoinvent 3.10 proxy, inland waterways
Conveyor and coal mill electricity (grid) | kWh | 0.794 | 0.0021 | 0.0013 | 0.0042 | 0.00072 | 0 | 0 | Jamali grid, active electricity mode
Sub-bituminous coal, 4200 kcal GAR, at gate | kg | 0.121 | 0.00098 | 0.00042 | 0.0021 | 0.00031 | 0 | 0 | ecoinvent 3.10 proxy, market for hard coal ID
FGD limestone | kg | 0.098 | 0.00021 | 0.00011 | 0.0004 | 5e-05 | 0 | 0 | ecoinvent 3.10 proxy, market for limestone
Process and make-up water | m3 | 0.34 | 0.00042 | 0.00021 | 0.0006 | 8e-05 | 0 | 0 | ecoinvent 3.10 proxy, tap water RoW
Controlled FABA landfilling | kg | 0.0079 | 3e-05 | 2e-05 | 5e-05 | 1e-05 | 0 | 0 | ecoinvent 3.10 proxy, inert waste landfill
Land use and water consumption are carried entirely by the foreground elementary flows, so the background columns are zero by construction.

## INDICATORS
CHARACTERISATION FACTORS — ReCiPe 2016 v1.03 midpoint (H)
Elementary flow | Compartment | Unit | GWP100 (kg CO2e) | Acidification (kg SO2e) | Photochem. ozone (kg NOxe) | PM formation (kg PM2.5e) | Freshwater eutroph. (kg Pe) | Land use (m2a) | Note
Allocated oil palm land occupation | raw | m2a | 0 | 0 | 0 | 0 | 0 | 1 | 0 | Crop-equivalent land occupation
CH4 biogenic — PKS stockpile | air | kg | 27 | 0 | 0 | 0 | 0 | 0 | 0 | AR5 GWP100, biogenic methane
Process and make-up water | raw | m3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | Consumptive water
CO2 fossil | air | kg | 1 | 0 | 0 | 0 | 0 | 0 | 0 | Reference substance
CO2 biogenic | air | kg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Reported separately, ISO 14067 clause 6.4.9
CH4 fossil — combustion | air | kg | 29.8 | 0 | 0 | 0 | 0 | 0 | 0 | AR5 GWP100, fossil methane
CH4 biogenic — combustion | air | kg | 27 | 0 | 0 | 0 | 0 | 0 | 0 | AR5 GWP100
N2O | air | kg | 273 | 0 | 0 | 0 | 0 | 0 | 0 | AR6 GWP100
NOx | air | kg | 0 | 0.36 | 1 | 0.11 | 0 | 0 | 0 | Acidification, ozone and secondary PM
SO2 | air | kg | 0 | 1 | 0 | 0.29 | 0 | 0 | 0 | Acidification and secondary PM
PM2.5 | air | kg | 0 | 0 | 0 | 1 | 0 | 0 | 0 | Primary particulate

## INVENTORY
LIFE CYCLE INVENTORY PER 1 MWh NET DELIVERED
Everything below the scenario drivers is a formula. Change a driver or a parameter and the whole inventory recomputes.
SCENARIO DRIVERS (blue = input)
Item | Unit | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
Co-firing share, energy basis | % | 0 | 5 | 10 | 20 | 30 | Efficiency penalty rises with co-firing share: mill throughput, higher moisture and lower flame temperature (plant test data, 2025).
Road transport distance | km | 100 | 100 | 100 | 150 | 60
Barge transport distance | km | 0 | 0 | 0 | 0 | 350
Net plant efficiency | % | 33 | 32.7 | 32.3 | 31.7 | 31
DERIVED FUEL AND ENERGY BALANCE
Item | Unit | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
Fuel energy input | MJ/MWh | 10909.0909 | 11009.1743 | 11145.5108 | 11356.4669 | 11612.9032
Energy from coal | MJ/MWh | 10909.0909 | 10458.7156 | 10030.9598 | 9085.1735 | 8129.0323
Energy from PKS | MJ/MWh | 0 | 550.4587 | 1114.5511 | 2271.2934 | 3483.871
Coal consumption | kg/MWh | 585.6916 | 561.5116 | 538.5461 | 487.7684 | 436.4347
PKS consumption | kg/MWh | 0 | 32.3134 | 65.4271 | 133.331 | 204.5125
Total fuel mass | kg/MWh | 585.6916 | 593.825 | 603.9732 | 621.0993 | 640.9472
Sulphur input | kg/MWh | 2.3993 | 2.316 | 2.2381 | 2.0633 | 1.8878
Ash input | kg/MWh | 32.3858 | 32.0219 | 31.7492 | 30.9864 | 30.2916
TECHNOSPHERE INPUTS (rows aligned with the BACKGROUND sheet)
Technosphere flow | Unit | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
PKS upstream, economically allocated | kg | 0 | 32.3134 | 65.4271 | 133.331 | 204.5125 | P1_PKM
Drying heat from biomass residue | MJ | 0 | 27.4664 | 55.6131 | 113.3313 | 173.8357 | P2_Drying
Crusher electricity | kWh | 0 | 0.58423 | 1.1829 | 2.4106 | 3.6976 | P2_Drying
Truck transport, diesel 24 t | t.km | 0 | 3.2313 | 6.5427 | 19.9996 | 12.2708 | P3_Transport
Barge transport, 3000 DWT | t.km | 0 | 0 | 0 | 0 | 71.5794 | P3_Transport
Conveyor and coal mill electricity | kWh | 7.0517 | 7.1497 | 7.2718 | 7.478 | 7.717 | P4_Handling
Sub-bituminous coal, 4200 kcal GAR | kg | 585.6916 | 561.5116 | 538.5461 | 487.7684 | 436.4347 | P5_Generation
FGD limestone | kg | 3.3758 | 3.2586 | 3.149 | 2.903 | 2.6561 | P5_Generation
Process and make-up water | m3 | 1.8 | 1.8165 | 1.839 | 1.8738 | 1.9161 | P5_Generation
Controlled FABA landfilling | kg | 29.3092 | 28.9798 | 28.7331 | 28.0427 | 27.4139 | P6_Ash
ELEMENTARY FLOWS (rows aligned with the INDICATORS sheet)
Elementary flow | Unit | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
Allocated oil palm land occupation | m2a | 0 | 13.5716 | 27.4794 | 55.999 | 85.8953 | P1_PKM
CH4 biogenic — PKS stockpile | kg | 0 | 0.0071002 | 0.014376 | 0.029297 | 0.044938 | P2_Drying
Process and make-up water | m3 | 1.8 | 1.8165 | 1.839 | 1.8738 | 1.9161 | P5_Generation
CO2 fossil | kg | 1032 | 989.3945 | 948.9288 | 859.4574 | 769.0065 | P5_Generation
CO2 biogenic | kg | 0 | 60.5505 | 122.6006 | 249.8423 | 383.2258 | P5_Generation
CH4 fossil — combustion | kg | 0.010909 | 0.010459 | 0.010031 | 0.0090852 | 0.008129 | P5_Generation
CH4 biogenic — combustion | kg | 0 | 0.00055046 | 0.0011146 | 0.0022713 | 0.0034839 | P5_Generation
N2O | kg | 0.016364 | 0.016514 | 0.016718 | 0.017035 | 0.017419 | P5_Generation
NOx | kg | 1.62 | 1.5879 | 1.56 | 1.4925 | 1.4271 | P5_Generation
SO2 | kg | 2.15 | 2.0741 | 2.0031 | 1.8439 | 1.6839 | P5_Generation
PM2.5 | kg | 0.088004 | 0.086789 | 0.085817 | 0.083269 | 0.080883 | P5_Generation
Cross-check: the 0% column reproduces the metered 2025 baseline inventory of Unit #2 (coal flow meter, CEMS, weighbridge).

## IMPACT ASSESSMENT
LIFE CYCLE IMPACT ASSESSMENT PER 1 MWh NET DELIVERED
Background term = inventory x BACKGROUND factors. Foreground term = inventory x INDICATORS characterisation factors.
Active electricity background: Attributional grid average, time of use 2025
1. GWP100 (climate change) | kg CO2-eq
Contribution | Unit | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
Background (upstream and ancillary) | kg CO2-eq | 77.6421 | 77.2455 | 77.0795 | 77.2639 | 77.8252
Foreground (direct emissions and resources) | kg CO2-eq | 1036.7924 | 994.421 | 954.2101 | 865.231 | 775.3116
TOTAL | kg CO2-eq | 1114.4345 | 1071.6665 | 1031.2895 | 942.4948 | 853.1368
Memo: biogenic CO2 (reported separately, ISO 14067) | kg CO2 | 0 | 60.5505 | 122.6006 | 249.8423 | 383.2258
Reduction vs baseline | % | 0% | 3.838% | 7.461% | 15.43% | 23.45%
2. Terrestrial acidification | kg SO2-eq
Contribution | Unit | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
Background (upstream and ancillary) | kg SO2-eq | 0.59113 | 0.58417 | 0.57887 | 0.57015 | 0.57377
Foreground (direct emissions and resources) | kg SO2-eq | 2.7332 | 2.6458 | 2.5647 | 2.3812 | 2.1977
TOTAL | kg SO2-eq | 3.3243 | 3.2299 | 3.1435 | 2.9513 | 2.7715
3. Photochemical ozone formation | kg NOx-eq
Contribution | Unit | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
Background (upstream and ancillary) | kg NOx-eq | 0.25649 | 0.26057 | 0.26554 | 0.27779 | 0.3224
Foreground (direct emissions and resources) | kg NOx-eq | 1.62 | 1.5879 | 1.56 | 1.4925 | 1.4271
TOTAL | kg NOx-eq | 1.8765 | 1.8484 | 1.8255 | 1.7703 | 1.7495
4. Fine particulate matter formation | kg PM2.5-eq
Contribution | Unit | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
Background (upstream and ancillary) | kg PM2.5-eq | 1.2635 | 1.2462 | 1.2324 | 1.2082 | 1.212
Foreground (direct emissions and resources) | kg PM2.5-eq | 0.88969 | 0.86296 | 0.83831 | 0.78217 | 0.72621
TOTAL | kg PM2.5-eq | 2.1532 | 2.1092 | 2.0707 | 1.9904 | 1.9382
5. Freshwater eutrophication | kg P-eq
Contribution | Unit | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
Background (upstream and ancillary) | kg P-eq | 0.18725 | 0.18584 | 0.18498 | 0.1839 | 0.18371
Foreground (direct emissions and resources) | kg P-eq | 0 | 0 | 0 | 0 | 0
TOTAL | kg P-eq | 0.18725 | 0.18584 | 0.18498 | 0.1839 | 0.18371
6. Land use | m2a crop-eq
Contribution | Unit | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
Background (upstream and ancillary) | m2a crop-eq | 0 | 0 | 0 | 0 | 0
Foreground (direct emissions and resources) | m2a crop-eq | 0 | 13.5716 | 27.4794 | 55.999 | 85.8953
TOTAL | m2a crop-eq | 0 | 13.5716 | 27.4794 | 55.999 | 85.8953
7. Water consumption | m3
Contribution | Unit | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
Background (upstream and ancillary) | m3 | 0 | 0 | 0 | 0 | 0
Foreground (direct emissions and resources) | m3 | 1.8 | 1.8165 | 1.839 | 1.8738 | 1.9161
TOTAL | m3 | 1.8 | 1.8165 | 1.839 | 1.8738 | 1.9161

## INTERPRETATION
INTERPRETATION — contribution, uncertainty and key drivers (ISO 14044 clause 4.5)
1. Climate result and stage contribution (kg CO2e per MWh)
Life cycle stage | Unit | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
P1_PKM — allocated PKS upstream | kg CO2-eq | 0 | 1.3895 | 2.8134 | 5.7332 | 8.794
P2_Drying — drying and crushing | kg CO2-eq | 0 | 0.77094 | 1.561 | 3.181 | 4.8793
P3_Transport — truck and barge | kg CO2-eq | 0 | 0.49116 | 0.99449 | 3.0399 | 5.301
P4_Handling — conveying and milling | kg CO2-eq | 5.5991 | 5.6768 | 5.7738 | 5.9376 | 6.1273
P5_Generation — combustion, reagents, water | kg CO2-eq | 1108.6039 | 1063.1092 | 1019.9198 | 924.3815 | 827.8186
P6_Ash — controlled FABA landfilling | kg CO2-eq | 0.23154 | 0.22894 | 0.22699 | 0.22154 | 0.21657
Total (check against IMPACT ASSESSMENT) | kg CO2-eq | 1114.4345 | 1071.6665 | 1031.2895 | 942.4948 | 853.1368
Difference vs IMPACT ASSESSMENT total | kg CO2-eq | 0 | 0 | 0 | 0 | 0
Share of total carried by direct combustion | % | 99.48% | 99.2% | 98.9% | 98.08% | 97.03%
2. Uncertainty — pedigree-weighted Monte Carlo, 1 000 iterations, seed 20250617
Statistic | Unit | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
Mean | kg CO2-eq | 1131.03 | 1122.03 | 1052.94 | 972.91 | 894.43 | Imported from the Brightway2 Monte Carlo run (output/monte_carlo.csv). Distributions are lognormal with pedigree-matrix geometric standard deviations.
Median | kg CO2-eq | 1122.98 | 1098.18 | 1021.72 | 946.59 | 878.86
5th percentile | kg CO2-eq | 741.43 | 737.83 | 681.47 | 621.32 | 584.98
95th percentile | kg CO2-eq | 1504.35 | 1595.27 | 1528.34 | 1377.31 | 1252.19
Coefficient of variation | % | 21.4 | 24.4 | 25.7 | 24 | 23.1
P(lower than baseline) | - | 0 | 0.535 | 0.595 | 0.69 | 0.785
Deterministic result | kg CO2-eq | 1114.4345 | 1071.6665 | 1031.2895 | 942.4948 | 853.1368
Mean / deterministic ratio | - | 1.0149 | 1.047 | 1.021 | 1.0323 | 1.0484
3. Key drivers — Sobol variance decomposition (30% co-firing case)
Parameter | First order S1 | Total order ST | Share of variance | Interpretation
Coal CO2 emission factor | 1.1007 | 1.1614 | 99.44% | Dominant — the result is essentially a coal-carbon calculation
Coal lower heating value | 0.00565 | 0.00561 | 0.4803% | Second order; sets how much coal is burnt per MJ
PKS lower heating value | -0.02538 | 0.00081 | 0.06936% | Matters only through the substituted coal mass
Auxiliary electricity intensity | 0.00019 | 6e-05 | 0.005137% | Negligible at plant scale
Crusher electricity | -0.00011 | 2e-05 | 0.001712% | Negligible
Stockpile methane | -1e-05 | 2.7e-06 | 0.0002312% | Negligible despite the worst pedigree score
Drying heat demand | 0 | 8e-07 | 6.85e-05% | Negligible — biomass residue heat
PKS CO2 emission factor | 0 | 0 | 0% | Zero by construction: biogenic carbon is characterised at 0
4. Completeness, consistency and conclusions
Completeness check | All flows above the 1% cut-off are included for every scenario; no data gap remains in the foreground. Background coverage relies on proxy datasets, declared as a limitation.
Consistency check | The same functional unit, allocation rule, cut-off and characterisation set are applied to every scenario; only the co-firing share, transport distances and net efficiency change.
Sensitivity check | The ranking of scenarios is unchanged across all four electricity background models and across the full Monte Carlo range for shares of 10% and above.
Main conclusion | Co-firing reduces the climate footprint of delivered electricity approximately linearly at about 8.7 kg CO2e per MWh per percentage point of co-firing, but the efficiency penalty absorbs roughly a quarter of the theoretical benefit.
Caveat on low shares | At 5% co-firing the probability of being better than the baseline is only 0.535 — statistically indistinguishable from no change once data quality is accounted for.
Burden shifting | Land occupation rises from zero to about 86 m2a per MWh and water consumption by around 6%, while acidification, ozone formation and particulate formation all fall.

## FUEL PRICES
FUEL PRICES AND MACRO-ECONOMIC ASSUMPTIONS (real 2026 terms)
Item | Value | Unit | Source / basis
Exchange rate | 16300 | IDR/USD | Bank Indonesia reference rate, mid-2026 working assumption
Coal delivered price, 4200 kcal GAR | 750000 | IDR/tonne | DMO benchmark for 4200 GAR (about USD 46/t) plus inland freight to the jetty
PKS delivered price at plant gate | 900000 | IDR/tonne | 2025-2026 Sumatra/Kalimantan mill-gate band Rp 750 000 - 1 200 000 plus handling
PKS price — low band | 750000 | IDR/tonne | Mill-gate price in a surplus season, short haul
PKS price — high band | 1200000 | IDR/tonne | Export-linked price, competition from pellet exporters
Domestic carbon price | 60000 | IDR/tCO2e | IDXCarbon traded range 2025-2026 (about USD 3.7/tCO2e)
Weighted average cost of capital, real | 0.1 | fraction | Utility-scale IPP hurdle rate in IDR real terms
Evaluation period | 25 | years | Remaining technical life of the unit after retrofit
Unit net capacity | 300 | MW | PLTU Unit #2 nameplate, net of own use
Capacity factor | 0.65 | fraction | 2025 despatch record for the unit
FGD limestone delivered | 480000 | IDR/tonne | Reagent purchase records 2025
Controlled FABA disposal | 180000 | IDR/tonne | B3 landfill gate fee and haulage
Process water | 4500 | IDR/m3 | Water treatment plant operating cost
Own-use electricity opportunity value | 1100 | IDR/kWh | Regional BPP for the Java-Bali system
DERIVED QUANTITIES
Annual net generation | 1708200 | MWh/year
Capital recovery factor | 0.11017 | 1/year
Coal price in USD | 46.0123 | USD/tonne
PKS price in USD | 55.2147 | USD/tonne

## CAPEX
RETROFIT CAPITAL EXPENDITURE (IDR, real 2026)
Reference package sized for 30% co-firing; other shares are scaled with a 0.7 capacity exponent, the usual convention for bulk handling equipment.
REFERENCE PACKAGE AT 30% CO-FIRING (blue = input)
Cost element | Amount (IDR) | Unit | Basis
Covered PKS storage, reclaim and yard civil works | 85000000000 | IDR | Two 5 000 t covered stores, reclaimer, drainage
Rotary dryer and hot-gas duct | 45000000000 | IDR | Biomass residue fired dryer sized for 30% share
Crusher, screening and dedicated feeders | 38000000000 | IDR | Two-stage crushing to below 6 mm
Mill and burner modification | 60000000000 | IDR | Classifier and burner tip changes on four mills
Conveyors, blending and dust suppression | 32000000000 | IDR | Blending on the common belt before the bunkers
Fire detection, explosion relief and instrumentation | 15000000000 | IDR | Biomass dust hazard mitigation
Control system, CEMS and reporting upgrade | 12000000000 | IDR | Fuel-blend accounting for the co-firing claim
Jetty and barge unloading upgrade | 40000000000 | IDR | Only needed for the barge-supplied 30% case
Engineering, permits and owner cost | 28000000000 | IDR | 10% of direct cost
Subtotal, direct and indirect | 355000000000
Contingency | 53250000000
Contingency rate | 15%
REFERENCE CAPEX AT 30% CO-FIRING | 408250000000
Reference CAPEX excluding the jetty package (road-supplied cases) | 362250000000
Reference share for the package | 30
Scaling exponent | 0.7
CAPEX BY SCENARIO
Item | Unit | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
Co-firing share | % | 0 | 5 | 10 | 20 | 30
Jetty upgrade required? | - | No | No | No | No | Yes
Scaled retrofit CAPEX | IDR | 0 | 103348105261.861 | 167889492315.6461 | 272737284912.8306 | 408250000000
CAPEX in USD | USD | 0 | 6340374.5559 | 10299968.8537 | 16732348.7677 | 25046012.2699
Specific CAPEX per kW installed | USD/kW | 0 | 21.1346 | 34.3332 | 55.7745 | 83.4867
The jetty and barge unloading package is charged only to the 30% barge-supplied case; the smaller shares are served by the existing road route.

## OPEX
ANNUAL OPERATING EXPENDITURE (IDR/year, real 2026)
Fuel and consumable quantities are pulled from the INVENTORY sheet and multiplied by annual generation.
Item | Unit | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
Coal purchase | IDR/yr | 750358736077.6235 | 719380623120.2904 | 689958342461.4681 | 624904436354.8663 | 559138283980.4227
PKS purchase | IDR/yr | 0 | 49677970072.4089 | 100586354264.2584 | 204980393863.4413 | 314413475103.4398
Road transport surcharge | IDR/yr | 0 | 6899718065.6123 | 13970326981.147 | 42704248721.5503 | 26201122925.2866
Barge transport surcharge | IDR/yr | 0 | 0 | 0 | 0 | 39127010235.0947
FGD limestone | IDR/yr | 2767935551.4977 | 2671873456.2185 | 2582001573.9092 | 2380297428.2369 | 2177813100.4178
Process water | IDR/yr | 13836420000 | 13963359633.0275 | 14136280495.356 | 14403844164.0379 | 14729092258.0645
FABA disposal | IDR/yr | 9011863946.8387 | 8910599942.281 | 8834728358.4985 | 8622458729.127 | 8429101853.1338
Additional own-use electricity (drying and crushing) | IDR/yr | 0 | 1097772743.1112 | 2222734904.0084 | 4529611192.3957 | 6947839103.1747
Fixed O&M uplift on the retrofit | IDR/yr | 0 | 3100443157.8558 | 5036684769.4694 | 8182118547.3849 | 12247500000
Variable O&M uplift, biomass handling | IDR/yr | 0 | 2318305270.0458 | 4694029865.6654 | 9565751713.6273 | 14672628838.1605
TOTAL ANNUAL OPEX | IDR/yr | 775974955575.96 | 808020665460.8514 | 842021483673.7805 | 920273160714.6675 | 998083867397.1953
Incremental OPEX vs baseline | IDR/yr | 0 | 32045709884.8915 | 66046528097.8206 | 144298205138.7075 | 222108911821.2354
OPEX per MWh | IDR/MWh | 454264.6971 | 473024.6256 | 492929.0971 | 538738.5322 | 584289.8182
OPEX RATE INPUTS
Rate | Value | Unit | Basis
Road freight tariff | 1250 | IDR/t.km | Contracted 24 t lorry rate, Sumatra-Java corridor 2026
Coastal barge tariff | 320 | IDR/t.km | 3 000 DWT barge charter, bulk biomass
Fixed O&M as share of retrofit CAPEX | 3% | fraction/yr | Additional inspection, dust housekeeping, fire watch
Variable O&M per tonne of PKS handled | 42000 | IDR/tonne | Extra manning, wear parts, sampling and lab

## CASH FLOW
25-YEAR INCREMENTAL CASH FLOW (IDR, real terms, discounted at the WACC)
Year 0 carries the retrofit CAPEX; years 1-25 carry total annual OPEX. LCOE is the ratio of discounted cost to discounted energy.
Year | Discount factor | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
0 | 1 | 0 | -103348105261.861 | -167889492315.6461 | -272737284912.8306 | -408250000000
1 | 0.90909 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
2 | 0.82645 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
3 | 0.75131 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
4 | 0.68301 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
5 | 0.62092 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
6 | 0.56447 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
7 | 0.51316 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
8 | 0.46651 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
9 | 0.4241 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
10 | 0.38554 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
11 | 0.35049 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
12 | 0.31863 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
13 | 0.28966 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
14 | 0.26333 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
15 | 0.23939 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
16 | 0.21763 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
17 | 0.19784 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
18 | 0.17986 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
19 | 0.16351 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
20 | 0.14864 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
21 | 0.13513 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
22 | 0.12285 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
23 | 0.11168 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
24 | 0.10153 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
25 | 0.092296 | -775974955575.96 | -808020665460.8514 | -842021483673.7805 | -920273160714.6675 | -998083867397.1953
NPV cost |  | 7.0436e+12 | 7.4378e+12 | 7.811e+12 | 8.6261e+12 | 9.4679e+12
Discounted energy | MWh | 15505399.7591 | 15505399.7591 | 15505399.7591 | 15505399.7591 | 15505399.7591
Fuel-and-O&M LCOE | IDR/MWh | 454264.6971 | 479689.9233 | 503756.9052 | 556328.3583 | 610619.3554
The cash flow is incremental in the sense that it excludes the sunk capital of the existing unit; both baseline and co-firing cases carry their full fuel and consumable cost, so the difference between columns is the true cost of co-firing.

## LCOE
LEVELISED COST OF ELECTRICITY AND COST BUILD-UP
Item | Unit | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
Annualised retrofit CAPEX | IDR/MWh | 0 | 6665.2977 | 10827.808 | 17589.8261 | 26329.5372
Coal cost | IDR/MWh | 439268.6665 | 421133.7215 | 403909.5788 | 365826.2711 | 327326.0063
PKS cost | IDR/MWh | 0 | 29082.0572 | 58884.413 | 119997.8889 | 184061.278
Transport surcharge | IDR/MWh | 0 | 4039.1746 | 8178.3907 | 24999.5602 | 38243.8433
Reagents, water and ash | IDR/MWh | 14996.0306 | 14954.8256 | 14959.0273 | 14873.3171 | 14831.9911
Own-use electricity | IDR/MWh | 0 | 642.6488 | 1301.2147 | 2651.6867 | 4067.3452
O&M uplift | IDR/MWh | 0 | 3172.1979 | 5696.4727 | 10389.8081 | 15759.3542
LCOE (annuity method) | IDR/MWh | 454264.6971 | 479689.9233 | 503756.9052 | 556328.3583 | 610619.3554
LCOE (discounted cash flow cross-check) | IDR/MWh | 454264.6971 | 479689.9233 | 503756.9052 | 556328.3583 | 610619.3554
LCOE in IDR/kWh | IDR/kWh | 454.2647 | 479.6899 | 503.7569 | 556.3284 | 610.6194
LCOE in USD/MWh | USD/MWh | 27.869 | 29.4288 | 30.9053 | 34.1306 | 37.4613
Increment vs baseline | IDR/MWh | 0 | 25425.2262 | 49492.2081 | 102063.6612 | 156354.6583
Increment vs baseline | % | 0% | 5.597% | 10.9% | 22.47% | 34.42%
The LCOE reported here is a fuel-and-operating LCOE for the existing unit: the sunk capital of the power block is excluded because it is identical in every scenario and does not affect the comparison.

## ABATEMENT COST
COST OF CARBON ABATEMENT AND BREAK-EVEN PKS PRICE
Item | Unit | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
Carbon footprint | kg CO2e/MWh | 1114.4345 | 1071.6665 | 1031.2895 | 942.4948 | 853.1368
Abatement vs baseline | kg CO2e/MWh | 0 | 42.768 | 83.145 | 171.9396 | 261.2977
Annual abatement | tCO2e/yr | 0 | 73056.2716 | 142028.2496 | 293707.3076 | 446348.6986
Incremental LCOE | IDR/MWh | 0 | 25425.2262 | 49492.2081 | 102063.6612 | 156354.6583
Abatement cost | IDR/kg CO2e | - | 594.492 | 595.2519 | 593.6017 | 598.3775
Abatement cost | IDR/tCO2e | - | 594492.0329 | 595251.9307 | 593601.6624 | 598377.5199
Abatement cost | USD/tCO2e | - | 36.4719 | 36.5185 | 36.4173 | 36.7103
Value of abatement at the domestic carbon price | IDR/MWh | 0 | 2566.0791 | 4988.6986 | 10316.3789 | 15677.8609
Net cost after carbon revenue | IDR/MWh | 0 | 22859.1471 | 44503.5094 | 91747.2823 | 140676.7974
Carbon price needed to break even | IDR/tCO2e | - | 594492.0329 | 595251.9307 | 593601.6624 | 598377.5199
BREAK-EVEN PKS PRICE (price at which co-firing costs the same as the baseline)
Item | Unit | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
PKS consumed | t/MWh | 0 | 0.032313 | 0.065427 | 0.13333 | 0.20451
Non-fuel cost increment (CAPEX, O&M, transport, own use) | IDR/MWh | 0 | 14478.114 | 25966.8828 | 55508.1676 | 84236.0404
Break-even PKS price | IDR/tonne | - | -448052.9867 | -396882.5248 | -416318.581 | -411886.9391
Headroom against the assumed PKS price | IDR/tonne | - | -1348052.9867 | -1296882.5248 | -1316318.581 | -1311886.9391
A negative break-even price means co-firing cannot reach parity with coal at any purchase price, because the non-fuel cost increment alone exceeds the coal saving.

## SENSITIVITY
SENSITIVITY ANALYSIS — 30% co-firing case
One-at-a-time swings around the central case, and a two-way price grid. Blue cells are the low and high bounds.
1. Tornado — effect on abatement cost (IDR/tCO2e)
Variable | Central | Low bound | High bound | Cost at low | Cost at high | Swing
PKS delivered price (IDR/t) | 900000 | 750000 | 1200000 | 480975.4842 | 833181.5913 | 352206.1071
Coal delivered price (IDR/t) | 750000 | 600000 | 950000 | 512695.4275 | 712620.3097 | 199924.8822
Retrofit CAPEX (multiplier) | 1 | 0.7 | 1.4 | 568148.1618 | 638683.3307 | 70535.1689
WACC (real) | 0.1 | 0.07 | 0.14 | 576099.037 | 630692.1869 | 54593.1498
Capacity factor | 0.65 | 0.5 | 0.8 | 628606.878 | 579484.1711 | 49122.7069
Efficiency penalty at 30% (pp) | 2 | 1 | 3.5 | 544523.5431 | 679158.4851 | 134634.942
Barge tariff (IDR/t.km) | 320 | 220 | 480 | 570983.7115 | 642207.6132 | 71223.9017
Central abatement cost | 598377.5199 | IDR/tCO2e
2. Two-way grid — abatement cost (IDR/tCO2e) at 30% co-firing
Rows: PKS price (IDR/t) ¦ Columns: coal price (IDR/t)
PKS \ Coal | 600000 | 675000 | 750000 | 850000 | 950000
700000 | 527523.5646 | 484682.5185 | 441841.4723 | 384720.0774 | 327598.6825
800000 | 605791.5884 | 562950.5423 | 520109.4961 | 462988.1012 | 405866.7063
900000 | 684059.6122 | 641218.5661 | 598377.5199 | 541256.125 | 484134.7301
1000000 | 762327.636 | 719486.5898 | 676645.5437 | 619524.1488 | 562402.7539
1100000 | 840595.6598 | 797754.6136 | 754913.5675 | 697792.1726 | 640670.7777
1200000 | 918863.6836 | 876022.6374 | 833181.5913 | 776060.1964 | 718938.8015
3. Environmental sensitivity — electricity background model
Change the mode number on the PARAMETERS sheet (cell elec_mode) and every impact result updates. Reported GWP for 30% co-firing:
Current mode | Attributional grid average, time of use 2025
GWP at 30% co-firing | 853.1368
GWP at baseline | 1114.4345

## DASHBOARD
DASHBOARD — PKS CO-FIRING, LCA AND TEA SUMMARY
Electricity background in force: Attributional grid average, time of use 2025
Indicator | Unit | Baseline 0% | Co-firing 5% | Co-firing 10% | Co-firing 20% | Co-firing 30% (barge)
Carbon footprint | kg CO2e/MWh | 1114.4345 | 1071.6665 | 1031.2895 | 942.4948 | 853.1368
Reduction vs baseline | % | 0% | 3.838% | 7.461% | 15.43% | 23.45%
Biogenic CO2 (reported separately) | kg CO2/MWh | 0 | 60.5505 | 122.6006 | 249.8423 | 383.2258
Probability of beating the baseline | - | 0 | 0.535 | 0.595 | 0.69 | 0.785
Monte Carlo 5th-95th percentile | kg CO2e/MWh | 741.43 - 1504 | 737.83 - 1595 | 681.47 - 1528 | 621.32 - 1377 | 584.98 - 1252
Terrestrial acidification | kg SO2e/MWh | 3.3243 | 3.2299 | 3.1435 | 2.9513 | 2.7715
Fine particulate formation | kg PM2.5e/MWh | 2.1532 | 2.1092 | 2.0707 | 1.9904 | 1.9382
Land occupation | m2a/MWh | 0 | 13.5716 | 27.4794 | 55.999 | 85.8953
Water consumption | m3/MWh | 1.8 | 1.8165 | 1.839 | 1.8738 | 1.9161
PKS demand | t/year | 0 | 55197.7445 | 111762.6158 | 227755.9932 | 349348.3057
Coal displaced | t/year | 0 | 41304.1506 | 80533.8582 | 167272.3996 | 254960.6028
Retrofit CAPEX | IDR | 0 | 103348105261.861 | 167889492315.6461 | 272737284912.8306 | 408250000000
LCOE | IDR/MWh | 454264.6971 | 479689.9233 | 503756.9052 | 556328.3583 | 610619.3554
LCOE increment | IDR/MWh | 0 | 25425.2262 | 49492.2081 | 102063.6612 | 156354.6583
Annual abatement | tCO2e/yr | 0 | 73056.2716 | 142028.2496 | 293707.3076 | 446348.6986
Abatement cost | IDR/tCO2e | - | 594492.0329 | 595251.9307 | 593601.6624 | 598377.5199
Abatement cost | USD/tCO2e | - | 36.4719 | 36.5185 | 36.4173 | 36.7103
Break-even PKS price | IDR/tonne | - | -448052.9867 | -396882.5248 | -416318.581 | -411886.9391
Headline reading
• Co-firing lowers the delivered carbon footprint roughly linearly, but the efficiency penalty and the extra PKS mass eat about a quarter of the theoretical saving.
• At 5% the improvement is not statistically robust: the probability of beating the baseline is 0.535, essentially a coin toss once pedigree uncertainty is applied.
• Climate is governed almost entirely by the coal carbon factor; every supply-chain parameter together explains less than 3% of the variance.
• Economically the measure is a high-cost abatement lever at the assumed PKS price, and it becomes attractive only if the delivered PKS price falls below the break-even value shown above or a materially higher carbon price applies.
• Burden shifting is limited to land occupation and a small water increase; acidification, ozone formation and particulate formation all improve.

## SOURCE GUIDE
SOURCE GUIDE — provenance of every literal in this workbook
Sheet | Item | Source | Date / reference
PARAMETERS | Fuel LHV, ash, sulphur, nitrogen | Plant fuel laboratory, 2025 sample set, ASTM D5865 / D3174 / D4239 | Jan-Dec 2025, 40 samples
PARAMETERS | CO2, CH4, N2O emission factors | IPCC 2006 Guidelines Vol. 2 Ch. 2, Tables 2.2 and 2.3 | IPCC 2006
PARAMETERS | NOx, SO2, PM2.5 factors | Continuous emission monitoring system, Unit #2 annual mean | 2025 CEMS record
PARAMETERS | Auxiliary and crusher electricity | Plant own-use log and crusher nameplate/throughput record | 2025 operating log
PARAMETERS | Stockpile methane | Biomass storage literature — lowest pedigree score in the study | Literature, 2018-2023
PARAMETERS | Land occupation | Estate productivity 3.8 t CPO/ha/yr with economic allocation to PKS | Company visit, 17 June 2025
PARAMETERS | Grid emission factors | KESDM Java-Bali grid emission factor; marginal variants derived from RUPTL despatch logic | KESDM 2025; RUPTL 2021-2030
BACKGROUND | Upstream factors | ecoinvent 3.10-consistent proxy set, Indonesian markets where available | ecoinvent 3.10 proxy
INDICATORS | Characterisation factors | ReCiPe 2016 v1.03 midpoint (H); GWP100 from IPCC AR5/AR6 | ReCiPe 2016
INVENTORY | Scenario definitions | pks-cofiring-brightway/data/scenarios.csv | Model repository
INTERPRETATION | Monte Carlo statistics | pks-cofiring-brightway/output/monte_carlo.csv, 1 000 iterations, seed 20250617 | Model run 2026
INTERPRETATION | Sobol indices | pks-cofiring-brightway/output/sobol_indices.csv, SALib Saltelli sampling | Model run 2026
FUEL PRICES | Coal price | Domestic market obligation benchmark price for 4200 kcal GAR plus inland freight | KESDM HBA/DMO 2025-2026
FUEL PRICES | PKS price | Sumatra and Kalimantan mill-gate quotations, plus handling and margin | Trade quotations 2025-2026
FUEL PRICES | Carbon price | IDXCarbon traded price range | 2025-2026
FUEL PRICES | WACC, capacity factor | Utility-scale IPP hurdle rate; unit despatch record | 2025
CAPEX | Retrofit package cost | Vendor budgetary quotations and comparable Indonesian co-firing retrofits, scaled with a 0.7 exponent | 2025-2026 budget prices
OPEX | Freight tariffs | Contracted lorry rate and 3 000 DWT barge charter for bulk biomass | 2026 contracts
OPEX | O&M uplift | Additional manning, wear parts, sampling and fire watch for biomass handling | Plant estimate
Cut-off flows | Excluded flows | Lubricants, small chemical dosing, personnel transport, office energy — each below 1% of mass, energy and environmental relevance | Cut-off register